## 2025 Support Emails
Date | Subject | System Category | System | Stream | Complexity | Business Impact | Your Action | Evidence Snippet | Reference
2025-02-03 | PCDI writes | Network (Modbus/PCDI) | SIS/Triconex | Routine Support | Low | Safety | Consulted SME on write anomalies during steam extraction control issue; validated Modscan/TMR observations. | Modscan confirmed no change (TMR Counts) | turn2search124
2025-02-04 | RE: SF#06871611/SF#06871612 - Recurring Experion PKS lost synchronization on redundant Server B. | DCS/Experion | Experion/TPS | Routine Support | Medium | Efficiency | Coordinated remote session; directed team to review EBR configuration (Section 2). | initiated the team call for a Remote Session to discuss the EBR configuration | turn2search106
2025-02-05 | RE: Case 00585587 - Ghost Historian Links and References | Integrity | Experion/TPS | Routine Support | Low | Compliance | Drove Integrity DB upgrade path to v7.3.1; requested EULA and change procedure for IT approval. | I’ll have to submit the 7.3.1 upgrade request to my IT department for approval | turn2search140
2025-02-05 | RE: Technical Question ¦ TPS & PLC5 References | DCS/Experion + Network | Experion/TPS | Legacy Modernization | Low | Low | Provided step-by-step mapping using TPS_EPLCG_* properties to link PLC-5 to TPS assets. | TPS_EPLCG_HWYNUM and TPS_EPLCG_BOXNUM correspond with the specific box | turn2search99
2025-03-25 | RE: 80672 Control Logix external cross reference with EPKS | Integrity/Network | Integrity (ALI) | Routine Support | Low | Production | Confirmed development guidance for CLX↔EPKS SCADA cross-references; unblocked asset modeling. | Users do not need to separate every SCADA point entry with a comma | turn2search82
2025-05-27 | RE: 00602281: Honeywell Experion UIO missing | DCS/Experion | Experion/TPS | Routine Support | Low | Efficiency | Standardized ODBC provider (Native Client 11) and re-ran EPKS imports to restore missing definitions. | got 362 definitions again | turn2search108
2025-06-16 | FW: Trident in ODC | SIS/Triconex | Experion/TPS | Unit Support | Low | Safety | Requested IP assignment to connect suitcase Trident trainer to ESVT0 for testing/training. | IP address assignment… Trident Trainer on LCN0 to talk with the Experion DCS (ESVT0) | turn2search114
2025-07-29 | FW: Cutover Tools blocked for HTU cutover | Other/Security Enablement | Experion/TPS | AMP/Cutover | Medium | Production | Coordinated Carbon Black exceptions to allow BAT-based cutover tools during TAR; clarified need for one-time vs. ongoing approvals. | Do the BAT files get constantly changed with new timestamps? | turn2search195
2025-08-05 | RE: P1 WO 1201083413 - Desox Loader Screen | PLC | PLC (Rockwell) | Routine Support | Medium | Production | Identified target PLC/HMI (Johnson Matthey Desox loader PLC) to focus troubleshooting. | Isn’t that the Johnson Mattey Desox loader PLC | turn2search210
2025-09-10 | FW: 15 Asset Hierarchy 250909 | Integrity | SIS/Triconex | Routine Support | Low | Low | Repaired and realigned asset hierarchy spreadsheet (vendor prefixes, TRX vs TS1131 naming). | many copy/paste mistakes… verify that we will use the TRX vs TS1131 | turn2search90
2025-09-25 | RE: MPC LAR Bently Nevada Integrity Data | GE/Woodward/Bently | Integrity (ALI) | L1 Integrity, Alarm Rationalization | Low | Low | Enumerated missing 3500 firmware assets; planned network access to harvest AssetInfo.txt files. | Looks like we are missing firmware files (AssetInfo.txt) for: | turn2search161
2025-10-07 | RE: Marathon ¦ St Paul ¦ Pre-Onsite Visit | Historian | Historian | Routine Support | Low | Production | Clarified PI vs. PHD architecture and suggested staging PI utilities post scope approval. | LAR did not include PHD since the corporate model is PI… OSI PI can be done later | turn2search138
2025-10-09 | RE: HCU TMR Alarm | SIS/Triconex | SIS/Triconex | Unit Support | Low | Safety | Referenced prior EDM training for pulling system faults; recommended shadowing for live troubleshooting. | Using EDM… covered in BC_LAR_ENGPRO001 | turn2search191
2025-10-21 | FW: LARINT01 - Cannot create scheduled task | Integrity | Experion/TPS | L1 Integrity, Legacy Modernization | High | Low | Documented export cadences (EXP/TPS) and reiterated scheduled task/batch needs for INT01. | EXP is usually done by Sat 5 AM; TPS by Monday 5 AM | turn2search101
2025-10-23 | WCC 92 Power Distribution Card Failure | GE/Woodward/Bently | GE/Woodward/Bently | Unit Support | Low | Compliance | Initiated follow-up on power distribution card incident; noted spare strategy considerations. | major mistake or isolation miss… Simplex hot spare | turn2search162
2025-12-08 | FW: Re: DSPPrime on TDC consoles | DCS/Experion (TDC/TPS) | Experion/TPS | Legacy Modernization | Low | Low | Shared dspprime/pntbld procedure to purge stale TDC points after cutover. | dspprime -sd … then … pntbld … -del | turn2search204
2025-12-11 | FW: FCC System Alarm 11SPLC30AO | Network (SCADA/Modbus) | PLC (Rockwell) | Unit Support | Low | Safety | Analyzed polling performance vs. register gaps; requested change chronology around 12/3. | tags that need to be pulled… in consecutive addresses | turn2search196
2025-12-11 | RE: APO 3.0 Installation | Alarm (APO) | Alarm Mgmt | Alarm Rationalization | Low | Safety | Raised L3/L4 edit constraints and CAR/PAR impacts; proposed template app/db servers and node rename procedure. | alternative architecture will have unintended consequences for CAR and PAR | turn2search142
2025-12-11 | RE: Console / Dynamo | Alarm (DynAMo) | Alarm Mgmt | Alarm Rationalization | Low | Safety | Explained suppression exposure vs. NTE reporting; reviewed specific NTE/level instruments. | If the alarm is suppressed, I don’t think it would show up in the report | turn2search226
2025-12-11 | RE: ETD_UTIL | Alarm (ACM/Tag Sync) | Alarm Mgmt | Routine Support | Low | Production | Provided Tag Sync add/delete lists and reasoning for In-Progress versions created by scheduled jobs. | Attached are the Add and Delete List generated by Tag Sync | turn2search217
2025-12-11 | RE: Significant issue with alarm discrepancies occurring between the servers and the consoles | DCS/Experion | Experion/TPS | Routine Support | Medium | Safety | Questioned BRM station role; supported EST rebuild plan and MOC path. | Is this a BRM Flex Station?… rebuild… into a full EST VM | turn2search193
2025-12-16 | SPW Dynamo Activities | Alarm (DynAMo) | Alarm Mgmt | Alarm Rationalization, Unit Support | Low | Safety | Investigated bulk UnSuppress actions and audit behavior across TPS/Experion. | system is bringing back… to the unsuppressed report as the auditing systems queries | turn2search207
2025-12-17 | RE: LCN3 (ALKY) DCS Backup and Integrity Update | DCS/Experion (TDC/TPS) | Experion/TPS | L1 Integrity, Alarm Rationalization, Unit Support | Low | Efficiency | Coordinated D3K EC schedules and executed backups for Carson LCNs; requested enabling ECs on ENG stations. | set up the… ECs again? I did run the backup on 12/5 | turn2search199
2025-12-19 | RE: LCN4 17XA861 and 84UA822 chattering alarms | Alarm (DynAMo/TPS) | Experion/TPS | Unit Support | Medium | Safety | Clarified INHIBIT vs DISABLE parity for suppression reporting; tied to journaling load relief. | INHIBIT vs DISABLE has no difference | turn2search132
2025-12-29 | RE: Integrity TS1131 cannot view XPS | SIS/Triconex + Integrity | SIS/Triconex | L1 Integrity, Alarm Rationalization, Legacy Modernization | High | Safety | Pursued PDF-based workaround and asked for model changes (Aha!) to move away from XPS. | A practical workaround… is to collect PDF files instead of XPS… Is that an AHA? | turn2search192
2025-12-29 | RE: ACM Secondary Parameter Update | Alarm (ACM) | Alarm Mgmt | Alarm Rationalization | Low | Safety | Ran secondary parameter update to push QB description/alarm edits; reported per-tag outcomes. | Tag updated successfully / Error. Tag not Updated | turn2search190
2025-12-29 | RE: ALERT: ACM DB Replication Heartbeat not implemented or cannot be detected | Alarm (ACM/M&R Replication) | Alarm Mgmt | Alarm Rationalization | High | Safety | Confirmed the replication/heartbeat condition self-recovered the following day. | fixed itself today (Monday 12/29) | turn2search224
2025-12-29 | RE: Zip files transferred correctly as well | Integrity | Integrity (ALI) | Routine Support | Low | Low | Verified transfer job execution from doublehop to INT01; set expectation on 8+ hour population. | slowly populating the transfer folder… normally takes like 8+ hours | turn2search220
2025-12-29 | RE: UDC Agents | Integrity/CyberIntegrity | Experion/TPS | L1 Integrity | Low | Low | Tracked redeploys across ESV/EVT fleet; highlighted remaining problematic nodes for follow-up. | Looks like only 2 remaining issues. ESVT4B; LAR6SHB-ESV11B | turn2search221
2025-12-31 | RE: DAS 91DAS005 | Alarm (Experion/DynAMo) | Experion/TPS | Routine Support | Low | Safety | Chased missing SUPP events on DAS triggers; captured re-init actions; warned about server-wide alarm toggling. | un-checked and re-checked Enable alarms server wide… not a normal troubleshooting step | turn2search188
2025-12-31 | RE: Trident DI Issues - LOV | SIS/Triconex + Integrity | SIS/Triconex | L1 Integrity, Alarm Rationalization | Low | Production | Pointed to CyberIntegrity inventory capability; noted current limitations in TRX component breakdown. | CyberIntegrity generates an inventory as well… doesn’t break out component controllers and IO | turn2search194