## Sheet1
Date | Project_Phase | Issue | Root_Cause | My_Role | Time_Spent | Was_This_Preventable
2024-02-26 | Graphics Performance Governance | Pushed back on system‑wide tuning; enforced HMIWeb display sizing analysis | Performance issue likely from display design, not system setting | Redirected team to sizing guidelines; avoid risky default changes | Not captured in email | Yes
2024-02-27 | Graphics Migration / HMI Upgrade (Post‑Project Problem) | Carson Coker graphic call‑up slowness (>5s) after TAR; suspected large subscription bursts | Over‑heavy displays / subscriptions | Requested deep analysis and sequencing before L1/L2 conversions | Not captured in email | Yes
2024-03-28 | C300 Installation (Design/Procurement) | Requested quote for redundant C300 EIM modules and IOTAs | Interface requirement for AB comms into C300 | Drove vendor quote for EIM + IOTA | Not captured in email | No
2024-05-07 | HMI Upgrade (Design/Installability) | Wilmington PSA HMI cabling/layout constraints; suggested thin‑client; minimized change‑order risk | Original physical layout constraints; risk of COs | Balanced design improvement vs CO risk; proceed with agreed rack | Not captured in email | Yes
2024-06-04 | Cutover / Migration Planning | Plan TDC (LCN3) console cutovers; evaluate ACE vs C300 for critical CMs | Legacy TDC/Hiway removal requires console changes; need placement strategy for critical calculations | Set technical direction; flagged evaluation of ACE short‑term vs C300 long‑term | Not captured in email | No
2024-09-06 | Console Upgrade (Planning/Execution) | FCC/HCU console consolidation scope and funding path alignment | Admin/funding alignment needed to move console work | Advised on IO/PO usage; unblocked contractor path | Not captured in email | No
2025-02-26 | Post‑Startup Sustainment | Coker C300 CKR_89 buffer exhaustion; degraded to request/response due to large subscriptions | HMI/graphics subscription load too high | Analyzed PI trends; highlighted outlier & probable cause | Not captured in email | Yes
2025-03-28 | ASM / Alarm Mgmt (Sustainment) | Established message‑alarm KPI monitoring per console with PI alerts | Lack of proactive KPI/alerting | Defined tags, historization, and alerting path | Not captured in email | Yes
2026-01-13 | FAT/SAT for Test Environment | Panel PC install failed—missing Panel Server option in license | Option omission in license/quote | Identified gap; requested quote for missing option | Not captured in email | Yes
2026-01-14 | Commissioning (SAT/Bring‑up) | ControlEdge UOC/PLC commissioning blocked by software/licensing on laptops/testbed | Missing/older builder installs and license readiness | Staged installers; coordinated license path & upgrades | Not captured in email | Yes
2026-01-14 | ASM Program (KPI Definition) | Proposed Alarm Flood KPI thresholds risked excessive CAT‑1 load; asked for data‑driven triggers | Thresholds proposed without site data review | Surfaced site data; requested evidence‑based thresholds | Not captured in email | Yes
2026-01-16 | Contractor Deliverable Quality | BGP+ visits—export bug & bulk operations caused data loss; incomplete deliverables | Known vendor defects; poor change‑control communication | Consolidated feedback; escalated expectations to Honeywell | Not captured in email | Yes
2026-01-20 | Project Handoff / RACI | Vendor continued changes on LARINT01 post‑turnover; unclear support role | Unclear RACI and access control after handoff | Challenged post‑handoff access; proposed removing corp admin group | Not captured in email | Yes