## Sheet1
Date | System | Summary | Stream | Complexity | Resolution | Business Impact
2026-01-06 | DCS: Experion, C300 | Provided Wilmington C300 checkpoint snapshot and Honeywell audit reference; recommended standardizing checkpoint/event archive settings across controllers. | Day-to-Day | Low | Informational | Efficiency
2026-01-08 | Integrity: Change management | Shared PMOC form for software change; noted applicability of steps for first deployment on live unit. | Project | Quick | Informational | Compliance
2026-01-22 | DCS: Experion, C300 | Investigated unexpected SP change on 3PC5140; traced to OP failure and module switchover; Instrument repaired water intrusion in valve positioner; SP stable; closed task. | Day-to-Day | Moderate | Fixed | Production
2026-01-19 | DCS: Experion (hardware) | Replaced HTU4 DCS power supply with Trey; cleared alarm and restored normal state. | Day-to-Day | Low | Fixed | Production
2026-01-20 | SIS: Trident | Cleared DI module fault in Trident via EDM; no recurrence after a week; closed item. | Day-to-Day | Low | Fixed | Safety
2026-01-23 | Network: Experion/ETD access | Troubleshot failed logins from ETD to clusters; removed ETD subscriptions and asked to confirm; planning TAC case. | Day-to-Day | Low | Pending | Efficiency
2026-01-07 | SIS: Triconex | Cleared fan-run first-out during hardware work; flagged logic change that will require MOC to prevent recurrence. | Project | Low | Pending | Safety
2026-01-08 | Other (facility monitoring) | Proposed temporary water leak detector tied to console alarms for ETD rack room until roof repair is verified. | Day-to-Day | Low | Pending | Efficiency
2026-01-19 | DCS: Experion (DO relay card) | Replaced DO relay card for ETD TK-158 timer valve; observed significant corrosion indicating late failure; unit back healthy. | Day-to-Day | Low | Fixed | Production
2026-01-05 | DCS: Experion, C300 | Documented New Year’s ETD leak impact; restored multiple IOMs/FTAs and returned controls to Ops. | Day-to-Day | High | Fixed | Production
2026-01-06 | SIS: Triconex / IPF logic | Sent prioritized list of HGU IPF alarms to investigate. | Diagnostic | Low | Pending | Safety
2026-01-12 | SIS: Trident | Reported CRU console IPF DI module fault; cleared via EDM; will monitor. | Day-to-Day | Low | Fixed | Safety
2026-01-22 | Integrity: I/O reservations | Issued AMP I/O reservation (ARF) for LAR6W existing points in 41-C300-1. | Project | Quick | Informational | Compliance
2026-01-21 | Alarm: Asset Intellect/DynAMo | Explained 13FY2000 alarm under asset; suggested cleanup plan. | Applications | Low | Informational | Compliance
2026-01-19 | SIS: Safety Manager | Advised on Safety Builder memory error; pointed to timerbase memory usage. | Applications | Low | Informational | Safety
2026-01-15 | APC: Blending (PBO) | Shared experience that PBO server restart resolved indicator issues. | Applications | Quick | Informational | Efficiency
2026-01-14 | DCS: Experion (RIO/IO Link) | Coordinated and confirmed Water Well #18 & Sub 8 RIO IO-Link cutovers; Ops verified control restored. | Project | Medium | Fixed | Production
2026-01-12 | SIS: Trident / Vendor case | Shared DO 3626X fault evidence; provided EDM screenshots to Schneider; awaiting guidance. | Day-to-Day | Low | Escalated | Safety
2026-01-08 | Other (facility remediation) | Requested Facilities address recurring ETD roof leaks; asked for plan/timeline. | Diagnostic | Low | Pending | Efficiency